## Solar Sizing
| Houston | Solar Irradiance in Houston, with fixed optimal angle, (kWhr/m^2/day)
| Solar Installation Capacity (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average | efficiency
|  | 3.53 | 3.87 | 4.65 | 4.98 | 5.2 | 5.2 | 5.4 | 5.24 | 5.19 | 4.75 | 3.93 | 3.51 | 4.6208 | 0.19253
predicted | 150 | 529.5 | 580.5 | 697.5 | 747 | 780 | 780 | 810 | 786 | 778.5 | 712.5 | 589.5 | 526.5 | 693.125 | (kWh/day) | 28.8802 | kWh/hr
|  | 22.0625 | 24.1875 | 29.0625 | 31.125 | 32.5 | 32.5 | 33.75 | 32.75 | 32.4375 | 29.6875 | 24.5625 | 21.9375 | 28.8802
|  | 14.7083 | 16.125 | 19.375 | 20.75 | 21.6667 | 21.6667 | 22.5 | 21.8333 | 21.625 | 19.7917 | 16.375 | 14.625 | 19.2535
| Palo Alto | Solar Irradiance in Houston, with fixed optimal angle, (kWhr/m^2/day) Jan: Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day)
| Solar Installation Capacity (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average | efficiency
|  | 2.38 | 3.26 | 4.7 | 6.31 | 7.3 | 7.82 | 7.41 | 6.66 | 5.45 | 4.14 | 2.79 | 2.14 | 5.03 | 0.20958
| S | 3.81 | 4.54 | 4.69 | 6.53 | 6.7 | 6.8 | 6.6 | 6.54 | 6.29 | 5.72 | 4.4 | 3.57 | 5.5158 | S
| 134 | 510.54 | 608.36 | 628.46 | 875.02 | 897.8 | 911.2 | 884.4 | 876.36 | 842.86 | 766.48 | 589.6 | 478.38 | 739.1217 | predicted S
predicted | 134 | 318.92 | 436.84 | 629.8 | 845.54 | 978.2 | 1047.88 | 992.94 | 892.44 | 730.3 | 554.76 | 373.86 | 286.76 | 674.02 | predicted w/ SSE
actual | 134 | 322.7228 | 517.9301 | 584.8156 | 820.5314 | 899.5895 | 923.8879 | 897.8282 | 820.7958 | 743.5082 | 575.8558 | 339.2348 | 282.4371 | 644.0948 | actual
| Note: | Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Jan: Mid-day in June, generation has reached ~115kW for approximately 3 ro 4 hr. This is near peak generation and not sustained.
|  | 13.4468 | 21.5804 | 24.3673 | 34.1888 | 37.4829 | 38.4953 | 37.4095 | 34.1998 | 30.9795 | 23.994 | 14.1348 | 11.7682 | 26.8373
|  | 10.0349 | 16.1048 | 18.1846 | 25.514 | 27.9723 | 28.7279 | 27.9175 | 25.5223 | 23.119 | 17.906 | 10.5483 | 8.7822 | 20.0278
Table of % total energy provided by solar panels over 1 year
Solar Installation Capacity (kW) - [not CEC]
| EcoPOD average Power Demand (kW) | Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Jan: 100; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Feb: 150; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Mar: 200; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Apr: 300; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) May: 500
| 50 | Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Jan: 34.66%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Feb: 51.98%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Mar: 69.31%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Apr: 104%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) May: 173.3%
| 100 | Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Jan: 17.33%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Feb: 25.99%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Mar: 34.66%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Apr: 51.98%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) May: 86.64%
| 200 | Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Jan: 8.664%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Feb: 13%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Mar: 17.33%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Apr: 25.99%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) May: 43.32%
| 250 | Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Jan: 6.931%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Feb: 10.4%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Mar: 13.86%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Apr: 20.79%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) May: 34.66%
| 300 | Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Jan: 5.776%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Feb: 8.664%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Mar: 11.55%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Apr: 17.33%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) May: 28.88%
| 450 | Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Jan: 3.851%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Feb: 5.776%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Mar: 7.701%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) Apr: 11.55%; Solar Irradiance in Palo Alto, with fixed optimal angle, (kWhr/m^2/day) May: 19.25%